## Part II
Topic | Question | Option1 | Option2 | Option3 | Option4 | answer
Day5 | As per provisions of IEGC, STU can not engage in | Planning and development of Inter-State Transmission System | Power Generation | Power Trading | Power Trading and Generation both | 3
Day5 | As per IEGC, Under Frequency Relays (UFRs) are to be provided for | Day to Day Load shedding to mange Load by States/UTs | Preventing the grid from cascade tripping and Grid Disintegration/ Grid Collapse | Protection of the Transmission Lines | Protection of Transformers | 2
Day5 | As per IEGC, Regional grids are to be operated as power pools | With centralised scheduling by RLDCs | With centralized scheduling by RLDC and NLDC | with decentralized scheduling and despatch, | None of these | 3
Day5 | Switching in/out of all 400 kV bus or line Reactors throughout the grid and Tap changing on all 400/220 kV ICTs shall be done | As per RLDCs instructions only. | As per decision by respective transmission Utility | As per decision by CTU | Any time as per decision by CPCC | 1
Day5 | As per IEGC who is responsible for discharging all functions of planning and co-ordination relating to inter-State transmission system in co-ordination with various agencies | Regional Power Committee (RPC) | Regional Load Despatch Centre (RLDC) | Central Transmission Utility (CTU) | Central Electricity Authority (CEA) | 3
Day5 | As per IEGC, Automatic Under-Frequency and df/dt Relays for load shedding in their respective systems are to be provided by | All SEBs, Distribution licensees and STUs | CTU and all STUs | Distribution licensees and STUs | CTU and all SEBs | 1
Day5 | After sheduling of forced outage of a unit under STOA, RLDC shall inform about the revised schedule to -------- | Seller | Buyer | Seller and Buyer | Either seller or Buyer | 3
Day5 | Automatic Voltage Regulator with digital control shall be mandatory in the generating unit of above | 500MW | 200 MW | 100 MW | 250 MW | 3
Day5 | Grid Connectivity Standards make it mandatory to have ‘two sets of batteries, each equipped with its own charger’ for sub-stations of | 220 kV and above | 132 kV and above | 66 kV and above | 400 kV and above | 2
Day5 | Request for making connection to inter state transmission system is to be made to | CTU | CEA | The licensee with whose system the inter-connection is proposed | CERC | 1
Day5 | The limit specified for the power factor of the distribution system and bulk consumer is | Not mentioned in CEA’s technical standards | Not less than 0.95 | Not less than 0.9 | Not less than 0.85 | 2
Day5 | AC Substations of 220 kV rating Auxilary supply shall be arranged from ……… independent sources of High Tension(HT) feeders | two | one | one with two LT transformers | Three | 1
Day5 | The governers of HYDRO generating units shall have a droop of …. | 5-10% | 5-8% | 4-6% | 3-6% | 4
Day5 | The penalty for non-compliance of CEA's Regulations can be imposed by | CEA | Appropriate Commission | Ministry of Power | Appellate Tribunal for Electricity | 2
Day5 | In a grid disturbance, generation loss is 19% but load loss is 22%. This grid disturbance will be classified as | GD 3 | GD 2 | GD 20 | Can't say | 1
Day5 | Mock exercises for fire fighting shall be conducted by the entities, ___ | once every 3 months | once every 6 months | once a year | once in 2 years | 3
Day5 | With reference to CEA's Grid Connectivity Standards, the preferable switching scheme for a 132 kV substation is: | main and transfer scheme | double main and transfer scheme | one and half breaker scheme | double bus double breaker scheme | 1
Day5 | The total harmonic distortion in 220 kV system shall not exceed: | 1.5% | 2% | 2.5% | 5% | 3
Day5 | The maximum possible voltage unbalance in 400 and 765 kV shall be: | 2% | 1.5% | 3% | 5% | 2
Day5 | The governor of a partially loaded generator senses that the frequency dipped from 50.0 to 49.9 Hz. As a result of governor action, the load angle of the machine will | increase | decrease | remain constant | decrease by 10 degrees | 1
Day5 | The reason that several generators on one bus of same capacity can operate at different power outputs while remaining interconnected and synchronised is that these are operating at different ____ | speeds | load angles | frequencies | voltages | 2
Day5 | To increase the power output from a generator, which one of the following actions should be performed? | increase the terminal voltage | increase the excitation | Increase the power input to the prime mover | Increase the terminal voltage and increase the excitation | 3
Day5 | What possible problems could be caused by continous low frequency operation, say 48Hz on a 50Hz system? | Gain of time on synchronous clocks | possible damage to turbine blades due to vibration at low speed | certain customers' equipment will run at higher than normal speed | None of these | 2
Day5 | If the speed droop of a 50Hz machine is 4%. What frequency drop must occur to effect a 25% load increase on that machine? | 2.0 Hz | 1.0 Hz | 0.5 Hz | 0.25Hz | 3
Day5 | If the system frequency is at 49.0 Hz then the RPM of a cylindrical rotor machine is ____ | 3000 | 2940 | 3060 | 2880 | 2
Day5 | Saturation of the core of a power transformer increases with ____ in frequency and _____ in voltage. | increase, decrease | increase, increase | decrease, decrease | decrease, increase | 4
Day5 | The kVAr rating required for improving the power factor of a load operating at 1000 kW and 0.8 power factor to 0.9 is ________. | 100 kVAr | 500 kVAr | 50 kVAr | 250 kVAr | 4
Day5 | Which of the following is/are the function/s of the series compensation (TCSC) ? | prevents the voltage collapse in heavily loaded lines | controls the power flow through parallel lines | controls the receiving end voltage | all of these | 4
Day5 | Match the FACTs controllers and their targets a)SVC,b)PST,c)TCSC::1)Load angle,2)Line reactance,3)Receiving end voltage | a-1,b-3,c-2 | a-3, b-1, c-2 | a-2,b-3,c-1 | a-3,b-2,c-1 | 2
Day5 | The transmission capacity of a transmission line with a SIL of P0 and a series compensation of Kse, is: | P0/Sqrt(1-Kse) | P0*Sqrt(1-Kse) | P0 * (1-Kse) | P0/(1-Kse) | 1
Day5 | The nearest kVAr compensation required for improving the power factor of a 500 kW load from 0.8 lag to unity power factor is | 375 kVAr | 100 kVAr | 500 kVAr | 250 KVAr | 1
Day5 | Real power output from a generator with respect to its excitation: ____ | directly proportional | inversely proportional | it remains unchanged | excitation is fixed and cannot be changed | 3
Day5 | Charging current in the transmission line _____ | lags the voltage by 90 degrees | leads the voltage by 45 degrees | leads the voltage by 90 degrees | leads the voltage by 180 degrees | 3
Day5 | Why are shunt reactors connected at receiving end of long transmission line system? | To increase terminal voltage | To compensate voltage rise caused by capacitive charging at light load | To improve power factor | To reduce the fault current | 2
Day5 | Safety Interlocks in Control schemes are: a) Isolator Open/Close possible only if CB is open b) E/S closing possible only when isolator is open | (a) only | (b) only | both (a) and (b) | Neither (a) nor (b) | 3
Day5 | Match the device numbers of relays: (a)distance (b) instantaneous over current (c) time delayed overcurrent (d) differential :: (1) 21; (2) 87; (3) 51; (4) 50 | a-1;b-2;c-3;d-4; | a-1; b-4; c-3; d-2 | a-4; b-3; c-1; d-2; | a-3; b-2; c-1; d-4; | 2
Day5 | The inrush current in a transformer contains predominantly | 7th harmonic | 2nd harmonic | 5th Harmonic | 3rd harmonic | 2
Day5 | Dead time for autoreclose is: | 1 minute | 1 sec | 5 minute | 10 milli sec | 2
Day5 | The time delay for Zone-3 in distance protection is: | 100-200 ms | 350-400ms | 1000-1200ms | 0 ms | 3
Day5 | Negative sequence Protection is used for: | Line | Transformer | Generator | Busbar | 3
Day5 | What Type of Auto-Reclosing arrangement is used in Indian Power System? | High Speed Single pole reclosing (HSAR) | High Speed Three pole reclosing (HTAR) | Delayed Three Pole reclosing (DAR) | Delayed auto reclosing (DAR) with dead line (DL) and synchronism check (SC) | 1
Day5 | The loss of field of a generator results in generator | stalling | running as induction generator | running as synchronous motor | over speeding | 2
Day5 | The extent of unbalance in the Generator / Motor currents are indicated by ______currents | Positive sequence | Negative sequence | Harmonic | Saturation | 2
Day5 | The winding of the transformer which may be used for protection as well as for serving load is called the ________ winding | Primary | Secondary | Tertiary | Auxiliary | 3
Day5 | Generally, a highly conneted substation has _________fault level. | High | Low | zero | Infinite | 1
Day5 | What is "NOT" an advantage of the switching substation? | Avoid switching surges | Easy segregation of faulty zones | Can be used as a pooling point | Feeding power to the local area | 4
Day5 | What is the primary function of earth mat in a substation? | To act as a foundation for all equipments | To act as a deterrent to rodents | To limit step and touch potential for substation staff | Provide a high impedance path to the fault currents | 3
Day5 | Surge arresters are provided to | Limit the fault current | To limit the voltage | To divert lightning surges to ground | To absorb switching, lighting surges and discharge | 4
Day5 | In a substation all non current carrying parts shall be connected to | Adjacent equipment | Separate Earth electrodes | Earth mat | Need not be earthed | 3
Day5 | Scada Functions are: | Data Acquisition | Data Processing | Alarms | All of the above | 4
Day5 | Define the range of values that SCADA uses to determine whether the value retrieved for the analog is realistic. | Normal limit | Reasonability Limit | Forbidden Limit | Dead band Limits | 2
Day5 | What type of flag appears when data is uninitialised ? | Good | Suspect | Calculated | Garbage | 4
Day5 | Breaker and switch status, Line analog parameters,Transformer analog parameters are the types of _____ | Distribution Data | Power Plant Data | Substation Data | System Operational Data | 3
Day5 | Historical data recording allows you to preserve time series of ____ | Analog | Digital | Both Analog and digital | only counter data | 3
Day5 | The assumption in Real Time Power system application of State Estimation are: | Voltage and current waveform are purely sinusoidal | Balanced 3 Ph System | 3 Ph. System described by positive sequence network | All of these | 4
Day5 | Which of the following is not taken as an input by the State Estimator application? | Voltage | Frequency | Reactive Power | Active Power | 2
Day5 | Which forecasting is useful in real-time operations? | Short Term Forecasting | Medium Term Forecasting | Long Term Forecasting | Very long term | 1