## Part I
Topic | Question | Option1 | Option2 | Option3 | Option4 | answer
Day3 | Energy consumption per unit of GDP is called as: | Energy Ratio | Energy Intensity | Per Capita Consumption | None | B
Day3 | Star rating is a part of ______ programme of BEE | DSM | BLY | S&L | None | C
Day3 | As per IEGC (latest amendment) “frequency band” in Hz is | 49.90 – 50.05 | 49.5 – 50.3 | 49.7 – 50.2 | 49.5 – 50.2 | A
Day3 | Action for non-compliance of IEGC may be taken by | Central Electricity Authority (CEA) on recommendation by RPC or RLDC | Regional Power Committee (RPC) on report by RLDC | Central Electricity Regulatory Commission(CERC) on report by RPC and RLDC only | Central Electricity Regulatory Commission(CERC) on report by any person or suo-motu | D
Day3 | A part of the grid can be deliberately isolated from the rest of the National/Regional grid, only | under an emergency, or to prevent collapse of grid | for safety of human life | when serious damage to a costly equipment is imminent and such isolation would prevent it, | All of these | D
Day3 | As per IEGC, free governor mode of operation (FGMO) is to be implemented for generating stations synchronized with grid ( with exceptions mentioned in IEGC) of the following category. | All coal/lignite based thermal generating units of 200MW and above Open cycle gas turbine/CCGT of capacity more than 50MW All hydro units of 25MW and above | All coal/lignite based thermal generating units of 200MW and above All hydro units of 25MW and above WS seller of capacity more than 10MW and connected at 33kV above | All coal/lignite based thermal generating units of 200MW and above Open cycle gas turbine/CCGT of capacity more than 50MW WS seller of capacity more than 10MW and connected at 33kV above | All coal/lignite based thermal generating units of 200MW and above Open cycle gas turbine/CCGT of capacity more than 50MW All hydro units of 25MW and above WS seller of capacity more than 10MW and connected at 33kV above | D
Day3 | As per stipulations in IEGC, the control Area jurisdiction of any generating station | Can not change once decided | May be in one control area (i.e. SLDC) at one point of time and another control area (i.e. RLDC) at another point of time | As decided by RPC | As decided by RLDC | B
Day3 | As per IEGC Var charges are applicable when | voltage at the metering point is below 97% | voltage is above103%. | In case of voltage below 97% or greater than 103% at the metering point. | Voltage at metering point is below 95 % or above 105 % | C
Day3 | If the state has quantum connectivity of more than 50% to Intra State Transmission System, for an IPP, then the scheduling and other functions shall be performed by----- | SLDC | RLDC | Neither SLDC nor RLDC | Either SLDC or RLDC | A
Day3 | If the state has quantum connectivity of 50% or less to Intra State Transmission System, for an IPP, then the scheduling and other functions shall be performed by----- | SLDC | RLDC | Neither SLDC nor RLDC | Either SLDC or RLDC | B
Day3 | A 'Bulk consumer' avails supply at : | 220 kV and above | 33 kV and above | 132 kV and above | 400 kV and above | B
Day3 | The maximum possible voltage unbalance in 33 to 132 kV shall be: | 2% | 1% | 3% | 5% | C
Day3 | The total harmonic distortion in 33 to 132 kV system shall not exceed: | 1.5% | 2% | 2.5% | 5% | D
Day3 | The category GI-1 incident means no loss of Grid integrity at : | 132 kV | 220 kV | 400 kV | 765 kV | B
Day3 | The category GD-2 disturbance means loss of __ % generation or load in the region | 0 to 10 | 10 to 20 | 20 to 30 | 30 to 40 | B
Day3 | With reference to CEA's Grid Connectivity Standards, the preferable switching scheme for a 220 kV substation is: | main and transfer scheme | double main and transfer bus scheme or double bus scheme | one and half breaker scheme or double main and transfer bus scheme | double bus double breaker scheme | B
Day3 | The maximum fault clearance time for system voltage of 220 kV is | 100 milliseconds | 160 milliseconds | 300 milliseconds | 100 microseconds | B
Day3 | Maximum Continuious Rating is determined | after deducting station auxilary load on manufacturer guarented rated MW | at the Genrator Terminals manufacturer guarented rated MW | after deducting station auxilary load on manufacturer guarented average MW/day | at the Genrator Terminals manufacturer guarented average MW/day | B
Day3 | The Generating transformer windings HV side need to achieve Earth Fault Factor of …. | 1.0 or more | 1.0 or less | 1.4 or more | 1.4 or less | D
Day3 | The governers of thermal generating units shall have a droop in the range of …. | 0-5 % | 5-8% | 3-8% | 3-6 % | D
Day3 | The total Harmonic Distortion of a 11 kV consumer for current drawn from transmission system at the connection point shall not exceed … | 10% | 5% | 3% | 8% | D
Day3 | Generation is a …… activity as per the Electricity Act 2003 | Licensed | Delicensed | Restricted | Commercial | B
Day3 | On which of the following fields does the Study Committee C2 of the International council on Large Electric Systems (CIGRE) deal with? | Electricity Markets | Equipment Standardisation | Environmental Concerns | System Operation and Control | D
Day3 | On which of the following fields does the Study Committee C5, of the International Council on Large Electric Systems (CIGRE) deal with? | Electricity Markets | Equipment Standardisation | Environmental Concerns | System Operation and Control | A
Day3 | If the voltages at ends A & B of a transmission line are 200∠30º kVand 220∠15ºkV respectively then, _____ | MW flows from A to B | MW flows from B to A | No MW flows in the line | Can not be determined from the given data | A
Day3 | The voltages at the two ends of a 400 kV line of 66 ohms reactance are 380∠0º and 408∠5º then steady state maximum power that can be transmitted in p.u is | 6.06 | 60.6 | 23.49 | 2.349 | C
Day3 | A long line having line reactor at one end should be charged from the end where there _________ line reactor. | Is a | Is no | Either end | None of the above | B
Day3 | Which option best describes the relation between Gross Station heat rate in a closed cycle operation and open cycle operation of a combined cycle gas station? | GSHR in closed cycle is same as in open cycle | GSHR in closed cycle is greater than than in open cycle | GSHR in open cycle is greater than than in closed cycle | It depends on the unit size | C
Day3 | The generator protection that is most likely to operate in a situation when there is "HIGH Voltage" and "LOW Frequency" in the grid: | Low forward power | Overflux | Differential | Loss of field | B
Day3 | What is the component which senses the frequency variations on the system and adjusts the MW output of the turbine generator called ? | exciter | governor | OLTC | frequency relay | B
Day3 | With reference to the turbine generator, the load angle is the phase angle difference between: | rotor and stator | turbine and generator | boiler and turbile | generator and transformer | A
Day3 | When the load angle exceeds the maximum limit, then the power output of the generator will _____ | increase | decrease | remains constant | increases by 100% | B
Day3 | In order that the frequency of the system remains constant, the electrical power output of the generator must be ___ the power required by the system load plus losses. | greater than | less than | equal to | No relationship | C
Day3 | What is the response of the turbine-governor when there is a drop in load? | The governor opens the turbine control valve to increase turbine input | The governor waits several minutes to see what happens | The governor closes the control valve position some what to decrease turbine input | None of the above | C
Day3 | Two machines, 'A' & 'B' of equal capacity have speed droop settings of 3% and 6% respectively. How will they share an increase in load? | Machine 'B' picks up large portion of load | Machine 'A' picks up large portion of load | Share the increase in load equally | Neither A nor B pick up the load | B
Day3 | Frequency response from loads is better in respect of: | Lighting load | Rotating loads | A combination of lighting loads and rotating loads | Silicon loads | B
Day3 | A generating unit running at 50 Hz and its rated capacity of 300 MW has 3 % speed droop. What will be the value of frequency if the unit's output requirement is reduced to 200 MW? | 50 Hz | 49.5 Hz | 50.5 Hz | 51.0 Hz | C
Day3 | If the system frequency is at 49.0 Hz then the RPM of a cylindrical rotor machine is ____ | 3000 | 2940 | 3060 | 2880 | B
Day3 | A 200 MW unit with 3% governor droop reduces its output from 180 MW to 160 MW under FGMO when the change in frequency is ___. | +0.15Hz | -0.15Hz | +0.3Hz | -0.3Hz | A
Day3 | Which of the following statements are correct: (i) Changing transformer taps change flow of VArs in the system. (ii) Shunt capacitors generate VArs and shunt reactors absorb Vars. (iii) Changing tap settings affect the flow of MW. | (i) & (iii) | (ii) & (iii) | (i), (ii) & (iii) | (i) & (ii) | D
Day3 | The kVAr rating required for improving the power factor of a load operating at 500 kW and 0.85 power factor to 0.95 is ________. | 145kVAr | 500 kVAr | 50 kVAr | 300 kVAr | A
Day3 | The resultant transmission capacity of a line having a SIL of P0, a shunt compensation of Ksh and a series compensation of Kse, is: | P0*(1-ksh) / (1-Kse) | P0*(1-Kse) / (1-Ksh) | P0*Sqrt(1-Ksh) / Sqrt(1-Kse) | P0*Sqrt(1-Kse) / Sqrt(1-Ksh) | C
Day3 | If a 40 MVAr reactor is connected at bus having 4000 MVA fault level and operating at 408 kV then the resultant bus voltage will be | 400 | 404 | 396 | 412 | B
Day3 | Which is the most suitable condition for operating OLTC of a 400kV/220kV auto transformer? | 390kV/220 kV | 410kV/201kV | 420kV/225kV | 380kV/180kV | B
Day3 | What do the SVC, CSR, UPFC, STATCOM devices control in common? | Receiving end voltage | Load angle | Line reactance | Sending end voltage | A
Day3 | Protection against Over voltage stage-I setting in p.u. is: | 1.1 | 1.5 | 0.95 | 1.3 | A
Day3 | Over flux alarm in a transformer is set at __ p.u. | 1 | 1.14 | 0.9 | 1.4 | B
Day3 | Through Fault current is ___. | The current flowing through a protected zone to a fault beyond that zone | The current flowing through a protected zone to a fault in the same zone | The current flowing through the protected device before fault | The post fault current flowing through the protected device | A
Day3 | Match the device numbers: (a)Circuit Breaker (b) Over voltage relay (c) earth fault relay (d) under voltage relay :: (1)64; (2) 59; (3) 52; (4)27 | a-2; b-4; c- 1; d- 3; | a-3; b-1; c-2; d-4 | a-3; b-2; c-1; d-4; | a-4;b-1;c-2;d-3 | C
Day3 | In the Master Station, packets are received by: | RTU | PLC | Communication Front End | Operator Console | C
Day3 | What is the system that provides the inter-connection of all the servers, workstation, peripherals with redundant ethernet switch? | WAN | LAN | DMZ | Ring main unit | B
Day3 | 'Milli seconds accurate time of status changes' for devices monitored, is provided by which application? | Historical Data Recorder | Sequence of Events | Network Management System | Human Machine Interface | B
Day3 | Which of these is true for network modeling in SCADA ? | Device Oriented model is used | SCADA analog measurements | SCADA digital measurements | All of the above | A
Day3 | State Estimation algorithm is based upon: | Weighted Least square Method | Newton Raphson Method | Decoupled Powerflow Method | Gauss-Siedel Method | A
Day3 | Fibre Optic Communication is based on: | Reflection of light | Total internal reflection of light | Refraction of light | Diffusion of light | B
Day3 | Which of these is not true for Fibre Optic medium? | Higher bandwidth | More susceptible to electromagnetic interference | Less signal degradation | Lighter and thinner than copper wire | B