## Sheet1
Topic | Question | Option1 | Option2 | Option3 | Option4 | answer
Day1 | Which of the following substation layouts sectionalizes the bus so that the entire substation is not shutdown in the event of a bus fault? | Single bus with tie breaker, ring bus | One and half breaker | Double bus double breaker | Main and Transfer | 1
Day1 | The winding of the transformer which may be used for protection as well as for serving load is called the ________ winding | Primary | Secondary | Tertiary | Auxiliary | 3
Day1 | What type of transformer is designed so that the primary and secondary windings are connected together? | Three winding transformer | Two winding transformer | Auto transformer | Converter transformer | 3
Day1 | What is certainly not available in a switching station ? Choose the best option | Transformer | Bus Reactor | Line Reactor | Series Capacitor | 1
Day1 | Which switching scheme does not require a bus coupler? | Double Main with transfer | Double Bus | Single Bus and Transfer | Single Bus with sectionalizer | 4
Day1 | Which switching arrangement does not require a separate bus bar protection? | Double bus | Ring bus | One and half breaker | Double Main with transfer | 2
Day1 | Which is the most widely used switching scheme at 400 kV level | Ring bus | Single Bus and Transfer | One and half breaker | Double bus | 3
Day1 | In a 400 kV substation having a breaker and a half scheme, how many breakers would have to be tripped to de energize a line which shares the dia with a ICT? | 1.5 | 3 | 1 | 2 | 4
Day1 | Which is the first equipment that would be encountered as one enters a substation (say 400 kV) from the line end? | Line CT | Wavetrap | Line CVT | Lightening Arrestor | 4
Day1 | Which is likely to be the most costly equipment in a substation? | Inter Connecting Transformer | Line Reactor | CT | Circuit Breaker | 1
Day1 | Bus Couplers are provided to: | Tie different buses | Segregate bus into number of sections | Isolate fault in bus | Synchronize | 1
Day1 | Instrument transformers are necessary | To operate protective relays | To record the current and voltages | To provide proportional current and voltage to relays, meters and synchronizing | To act as isolating device in high voltage system | 3
Day1 | Surge arresters are provided to | Limit the fault current | To limit the voltage | To divert lightning surges to ground | To absorb switching and lighting surges and discharge | 4
Day1 | In a substation all non current carrying parts shall be connected to | Adjacent equipment | Separate Earth electrodes | Earth mat | Need not be earthed | 3
Day1 | Earth Potential rise can be controlled by | Reducing the system voltage | Increasing the earth resistance | Increasing the area of Substation | Reducing the fault current and the earth resistance | 4
Day1 | Judgment of the appellate tribunal can be appealed against in: | Sessions Court | High Court | Supreme Court | Consumer court | 3
Day1 | Cross subsidy is that part of electricity cost realized from ___ | High End Consumer | Government | Public | Generation Company | 1
Day1 | Appeal from the order of the State Commission or the Central Commission can be preferred before which authority? | Disctrict court | Appellete Tribunal | High Court | Supreme Court | 2
Day1 | What is the time limitation for filing Appeal before the Appellate Tribunal? | 30 DAYS | 60 DAYS | 90 DAYS | 45 DAYS | 4
Day1 | Electricity Act, 2003 was promulgated after repealing which earlier enactment of Electricity Laws | Electtricity Act, 1910 | Electricity Supply Act, 1948 | The Electricity Regulatory Commssions Act, 1998 | All of these | 4
Day1 | What are the activities that are licensed under the new Elecitiricty Act, 2003 ? | Generation | Transmission | Distribution | Both Transmission and Distribution | 4
Day1 | Under which extraordinary circumstances is the appropriate government empowered to direct a genarating company to operate and maintain any generating station in accordance to their directions | a natural disaster/ calamity | threat to security of the state | any circumstance arising in public interst | all of these options | 4 | sec11
Day1 | The National Electricity Policy and the National Tariff Policy is prepared by the | Central Government | CERC | CEA | Central Government in consultation with the state governments and the CEA | 4
Day1 | The National Electricity Plan is notified | once a year | once in two years | once in five years | as and when felt appropriate | 3
Day1 | Non-compliance of directions issued by RLDCs/ SLDCs evokes a penalty of maximum | Rs. 5 lakhs | Rs. 10 lakhs | Rs. 15 lakhs | Rs. 20 lakhs | 3
Day1 | Which of the following is the main aim of the IE Act 2003 from its Preamble? | Govt.-strengthening | Competition | SEB-centric | job creation | 2
Day1 | Which of the following new organisations has been created under the Act. | SERC | CERC | Appellate Tribunal | Supreme Court | 3
Day1 | Who is entrusted with the framing of Electricity Policy? | State Government | Central Government | SERC | CERC | 2
Day1 | What do you understand by the term,'subordinate legislation'? | By State Legislatures | By Parliament Committees | Govt. Controls | Rules and Regulations | 4
Day1 | Who is to frame the Tariff policy? | Central Govt. | CERC | SERC | State Govt. | 1
Day1 | Who is to lay down the guidelines for Competitive bidding for tariff purposes? | State Govt | Central Govt | SERC | CERC | 2
Day1 | Which of the following is the appropriate reason for private sector participation under the Act? | Replace Public Sector | Replace the foreign Companies | Complement public sector | Efficiency | 3
Day1 | Which of the following lays down the Performance Standards in the Power Sector? | State Govt | Central Govt | SERC | CERC | 3
Day1 | Who has powers to nominate a state arbitrator under the Act? | High Court | State Govt. | SERC | CERC | 3
Day1 | Who appoints Electricity Ombudsman in a State? | State Govt | Central Govt | SERC | CERC | 3
Day1 | The nodal agency at the centre for implementing the EC act is | CEA | SDA | BEE | Ministry of Power | 3
Day1 | For Successful implementation of National Mission for Enhanced Energy Efficiency, which of the following initiatives are taken? | Perform , Achieve & Trade, Market Transformation for Energy Efficiency | Energy Efficiency Financing Platform | Framework For Energy Efficient Economic Development | All of these | 4
Day1 | Purpose of Demand Side Management (DSM) in Agriculture is | Reducing the overall power consumption | Improving efficiencies of ground water extraction | Reducing the subsidy burden of the states without sacrificing the service obligation to the sector | All of these | 4
Day1 | The National Policy for stand alone systems for rural areas shall be notified by | Central Government | CERC | CEA | Central Government in consultation with the state governments | 4
Day1 | The EC Act 2001 is applicabe to | Whole India | Whole India Except North Eastern States | Whole India Except Jammu & Kashmir | Whole India Except Union Teritories | 3
Day1 | As per Energy Conservation Act, 2001 Cycle means | the period of three years available to a designated consumer to comply with the energy consumption norms and standards | the period of five years available to a designated consumer to comply with the energy consumption norms and standards | the period of two years available to a designated consumer to comply with the energy consumption norms and standards | the period of ten years available to a designated consumer to comply with the energy consumption norms and standards | 1
Day1 | PAT means in EC Act 2001 is | Profit After Trade | Perfom After Trade | Perfrom Achieve Trade | Profit Achieve Trade | 3
Day1 | The number of ammendments made to the EC Act till date is | 1 | 2 | 3 | 4 | 2
Day1 | Who will specify the qualifications for the accredited energy auditors; | Central Government | CERC | CEA | BEE | 4
Day1 | The powers to alter the list of Energy Intensive Industries specified in the Schedule is with | BEE | Central Government | CEA | CERC | 2
Day1 | 500 MW power is being transferred from Area A to Area B limited by the transfer capabilty. A contingency in the system leads to voltages falling below 380 kV on the 400 kV bus. Which of the statements is true? | The ATC for Area A to Area B would become more than 500 MW. | 1000 MW can be easily transferred from Area B to Area A. | The ATC from Area A to Area B would become less than 500 MW. | 500 MW can be easily scheduled from Area A to Area B. | 3
Day1 | Area A is connected to areas B and C. There is no interconnection between Area B and C. The TTC from Area B to A is 1200 MW while the TTC from Area C to Area A is 700 MW. The simultaneous import capability of Area A would be: | greater than 1900 MW | 500 MW | Could be less than or equal to 1900 MW. | 1900 MW | 3
Day1 | The different limits to be considered while evaluating TTC are: | Stability, voltage and thermal limits | Sag, active power and reactive power | temperature, pressure and relative humidity | MVA | 1
Day1 | Which relationship between transfer capability and transmission capacity is generally the case? | Transfer capability is greater than transmission capacity | Both are equal to each other | Transfer capability is less than transmission capacity | None of these | 3
Day1 | Two 315 MVA, 400/220 kV interconnecting transformers are operating in parallel with the interconnected system. The transfer capability in the 400 kV to 220 kV direction is 400 MW. The transfer capability in the 220 kV to 400 kV direction would be: | 400 MW | Would have to be worked out from simulation studies | 630 MW | Zero | 2
Day1 | What would happen to the Surge Impedance Loading (SIL) of a twin Moose 400 kV line if its length is doubled? | No change | Doubles | Becomes half | Becomes four times. | 1
Day1 | The system operator gets a request for 700 MW open access contracts from System A to System B. The ATC between these two systems is however only 500 MW. What will the operator do? | Increase the TTC by 200 MW and approve all the open access requests. | Reduce reliability margin by 200 MW and approve all the open access requests. | Approve all the transactions and curtail in real time in case of a congestion | Issue a curtailed approval based on ATC. | 4
Day1 | Reliability is a combination of | Adequacy and security | Availability and dependability | Mean Time To Repair and Mean Time Between Failures | availability and optimal loading | 1
Day1 | Outage hours to customer makes sense as long as | VOLL is less than cost of providing peaking power | Consumer protection laws are lax | Does not make sense at all | None of the above | 1
Day1 | St. Clair curve gives the relationship between | Line loadability in terms of SIL versus line length | Line loading and voltage drop | Line loading and reactive power | None of the above | 1
Day1 | TRM is basically required for the purpose of | Mitigating uncertainty in system conditions | Help the system operator in real time | Barriers to free trade and restraint on traders | None of the above | 1
Day2 | Energy consumption per unit of GDP is called as: | Energy Ratio | Energy Intensity | Per Capita Consumption | None | 2
Day2 | Star rating is a part of ______ programme of BEE | DSM | BLY | S&L | None | 3
Day2 | As per IEGC (latest amendment) “frequency band” in Hz is | 49.90 – 50.05 | 49.5 – 50.3 | 49.7 – 50.2 | 49.5 – 50.2 | 1
Day2 | Action for non-compliance of IEGC may be taken by | Central Electricity Authority (CEA) on recommendation by RPC or RLDC | Regional Power Committee (RPC) on report by RLDC | Central Electricity Regulatory Commission(CERC) on report by RPC and RLDC only | Central Electricity Regulatory Commission(CERC) on report by any person or suo-motu | 4
Day2 | A part of the grid can be deliberately isolated from the rest of the National/Regional grid, only | under an emergency, or to prevent collapse of grid | for safety of human life | when serious damage to a costly equipment is imminent and such isolation would prevent it, | All of these | 4
Day2 | As per IEGC, restricted governor mode of operation is to be implemented for generating stations synchronized with grid ( with exceptions mentioned in IEGC) of the following category. | All thermal generating units of 200 MW and above | All hydro units (except those with upto three hours pondage) of 10 MW and above, | Thermal units >=200MW and Hydro units >=10MW owned by central sector Generating companys | All coal/lignite based thermal generating units of 200MWand above, open cycle gas turbine/CCGT of capacity more than 50MW and all hydro units of 25MW and above | 4
Day2 | As per stipulations in IEGC, the control Area jurisdiction of any generating station | Can not change once decided | May be in one control area (i.e. SLDC) at one point of time and another control area (i.e. RLDC) at another point of time | As decided by RPC | As decided by RLDC | 2
Day2 | As per IEGC Var charges are applicable when | voltage at the metering point is below 97% | voltage is above103%. | In case of voltage below 97% or greater than 103% at the metering point. | Voltage at metering point is below 95 % or above 105 % | 3
Day2 | If the state has a share of more than 50% in an IPP, then the scheduling and other functions shall be performed by----- | SLDC | RLDC | Neither SLDC nor RLDC | Either SLDC or RLDC | 1
Day2 | If the state has a share of 50% or less in an IPP, then the scheduling and other functions shall be performed by----- | SLDC | RLDC | Neither SLDC nor RLDC | Either SLDC or RLDC | 2
Day2 | A 'Bulk consumer' avails supply at : | 220 kV and above | 33 kV and above | 132 kV and above | 400 kV and above | 2
Day2 | The maximum possible voltage unbalance in 33 to 132 kV shall be: | 2% | 1% | 3% | 5% | 3
Day2 | The total harmonic distortion in 33 to 132 kV system shall not exceed: | 1.5% | 2% | 2.5% | 5% | 4
Day2 | The category GI-1 incident means no loss of Grid integrity at : | 132 kV | 220 kV | 400 kV | 765 kV | 2
Day2 | The category GD-2 disturbance means loss of __ % generation or load in the region | 0 to 10 | 10 to 20 | 20 to 30 | 30 to 40 | 2
Day2 | With reference to CEA's Grid Connectivity Standards, the preferable switching scheme for a 220 kV substation is: | main and transfer scheme | double main and transfer scheme or double main with breaker by pass scheme | one and half breaker scheme or double main and transfer bus scheme | double bus double breaker scheme | 2
Day2 | The maximum fault clearance time for system voltage of 220 kV is | 100 milliseconds | 160 milliseconds | 300 milliseconds | 100 microseconds | 2
Day2 | Maximum Continuious Rating is determined | after deducting station auxilary load on manufacturer guarented rated MW | at the Genrator Terminals manufacturer guarented rated MW | after deducting station auxilary load on manufacturer guarented average MW/day | at the Genrator Terminals manufacturer guarented average MW/day | 2
Day2 | The Generating transformer windings HV side need to achieve Earth Fault Factor of …. | 1.0 or more | 1.0 or less | 1.4 or more | 1.4 or less | 4
Day2 | The governers of thermal generating units shall have a droop in the range of …. | 0-5 % | 5-8% | 3-8% | 3-6 % | 4
Day2 | The total Harmonic Distortion of a 11 kV consumer for current drawn from transmission system at the connection point shall not exceed … | 10% | 5% | 3% | 8% | 4
Day2 | Generation is a …… activity as per the Electricity Act 2003 | Licensed | Delicensed | Restricted | Commercial | 2
Day2 | On which of the following fields does the Study Committee C2 of the International council on Large Electric Systems (CIGRE) deal with? | Electricity Markets | Equipment Standardisation | Environmental Concerns | System Operation and Control | 4
Day2 | On which of the following fields does the Study Committee C5, of the International Council on Large Electric Systems (CIGRE) deal with? | Electricity Markets | Equipment Standardisation | Environmental Concerns | System Operation and Control | 1
Day2 | If the voltages at ends A & B of a transmission line are 200∠30º kVand 220∠15ºkV respectively then, _____ | MW flows from A to B | MW flows from B to A | No MW flows in the line | Can not be determined from the given data | 1
Day2 | The voltages at the two ends of a 400 kV line of 66 ohms reactance are 380∠0º and 408∠5º then steady state maximum power that can be transmitted in p.u is | 6.06 | 60.6 | 23.49 | 2.349 | 3
Day2 | A long line having line reactor at one end should be charged from the end where there _________ line reactor. | Is a | Is no | Either end | None of the above | 2
Day2 | Which option best describes the relation between Gross Station heat rate in a closed cycle operation and open cycle operation of a combined cycle gas station? | GSHR in closed cycle is same as in open cycle | GSHR in closed cycle is greater than than in open cycle | GSHR in open cycle is greater than than in closed cycle | It depends on the unit size | 3
Day2 | The generator protection that is most likely to operate in a situation when there is "HIGH Voltage" and "LOW Frequency" in the grid: | Low forward power | Overflux | Differential | Loss of field | 2
Day2 | What is the component which senses the frequency variations on the system and adjusts the MW output of the turbine generator called ? | exciter | governor | OLTC | frequency relay | 2
Day2 | With reference to the turbine generator, the load angle is the phase angle difference between: | rotor and stator | turbine and generator | boiler and turbile | generator and transformer | 1
Day2 | When the load angle exceeds the maximum limit, then the power output of the generator will _____ | increase | decrease | remains constant | increases by 100% | 2
Day2 | In order that the frequency of the system remains constant, the electrical power output of the generator must be ___ the power required by the system load plus losses. | greater than | less than | equal to | No relationship | 3
Day2 | What is the response of the turbine-governor when there is a drop in load? | The governor opens the turbine control valve to increase turbine input | The governor waits several minutes to see what happens | The governor closes the control valve position some what to decrease turbine input | None of the above | 3
Day2 | Two machines, 'A' & 'B' of equal capacity have speed droop settings of 3% and 6% respectively. How will they share an increase in load? | Machine 'B' picks up large portion of load | Machine 'A' picks up large portion of load | Share the increase in load equally | Neither A nor B pick up the load | 2
Day2 | Frequency response from loads is better in respect of: | Lighting load | Rotating loads | A combination of lighting loads and rotating loads | Silicon loads | 2
Day2 | A generating unit running at 50 Hz and its rated capacity of 300 MW has 3 % speed droop. What will be the value of frequency if the unit's output requirement is reduced to 200 MW? | 50 Hz | 49.5 Hz | 50.5 Hz | 51.0 Hz | 3
Day2 | If the system frequency is at 49.0 Hz then the RPM of a cylindrical rotor machine is ____ | 3000 | 2940 | 3060 | 2880 | 2
Day2 | What is 'Load Rejection' ? | Under frequency Load shedding | Over frequency unit tripping | reduction in load with decrease in frequency | manual load shedding | 3
Day2 | A 200 MW unit with 3% governor droop reduces its output from 180 MW to 160 MW under FGMO when the change in frequency is ___. | +0.15Hz | -0.15Hz | +0.3Hz | -0.3Hz | 1
Day2 | Which of the following statements are correct: (i) Changing transformer taps change flow of VArs in the system. (ii) Shunt capacitors generate VArs and shunt reactors absorb Vars. (iii) Changing tap settings affect the flow of MW. | (i) & (iii) | (ii) & (iii) | (i), (ii) & (iii) | (i) & (ii) | 4
Day2 | The kVAr rating required for improving the power factor of a load operating at 500 kW and 0.85 power factor to 0.95 is ________. | 145kVAr | 500 kVAr | 50 kVAr | 300 kVAr | 1
Day2 | The resultant transmission capacity of a line having a SIL of P0, a shunt compensation of Ksh and a series compensation of Kse, is: | P0*(1-ksh) / (1-Kse) | P0*(1-Kse) / (1-Ksh) | P0*Sqrt(1-Ksh) / Sqrt(1-Kse) | P0*Sqrt(1-Kse) / Sqrt(1-Ksh) | 3
Day2 | If a 40 MVAr reactor is connected at bus having 4000 MVA fault level and operating at 408 kV then the resultant bus voltage will be | 400 | 404 | 396 | 412 | 2
Day2 | Which is the most suitable condition for operating OLTC of a 400kV/220kV auto transformer? | 390kV/220 kV | 410kV/201kV | 420kV/225kV | 380kV/180kV | 2
Day2 | What do the SVC, CSR, UPFC, STATCOM devices control in common? | Receiving end voltage | Load angle | Line reactance | Sending end voltage | 1
Day2 | Protection against Over voltage stage-I setting in p.u. is: | 1.1 | 1.5 | 0.95 | 1.3 | 1
Day2 | Over flux alarm in a transformer is set at __ p.u. | 1 | 1.14 | 0.9 | 1.4 | 2
Day2 | Through Fault current is ___. | The current flowing through a protected zone to a fault beyond that zone | The current flowing through a protected zone to a fault in the same zone | The current flowing through the protected device before fault | The post fault current flowing through the protected device | 1
Day2 | Match the device numbers: (a)Circuit Breaker (b) Over voltage relay (c) earth fault relay (d) under voltage relay :: (1)64; (2) 59; (3) 52; (4)27 | a-2; b-4; c- 1; d- 3; | a-3; b-1; c-2; d-4 | a-3; b-2; c-1; d-4; | a-4;b-1;c-2;d-3 | 3
Day2 | In the Master Station, packets are received by: | RTU | PLC | Communication Front End | Operator Console | 3
Day2 | What is the system that provides the inter-connection of all the servers, workstation, peripherals with redundant ethernet switch? | WAN | LAN | DMZ | Ring main unit | 2
Day2 | 'Milli seconds accurate time of status changes' for devices monitored, is provided by which application? | Historical Data Recorder | Sequence of Events | Network Management System | Human Machine Interface | 2
Day2 | Which of these is true for network modeling in SCADA ? | Device Oriented model is used | SCADA analog measurements | SCADA digital measurements | All of the above | 1
Day2 | State Estimation algorithm is based upon: | Weighted Least square Method | Newton Raphson Method | Decoupled Powerflow Method | Gauss-Siedel Method | 1
Day2 | Fibre Optic Communication is based on: | Reflection of light | Total internal reflection of light | Refraction of light | Diffusion of light | 2
Day2 | Which of these is not true for Fibre Optic medium? | Higher bandwidth | More susceptible to electromagnetic interference | Less signal degradation | Lighter and thinner than copper wire | 2
Day3 | As per provisions of IEGC, STU can not engage in | Planning and development of Inter-State Transmission System | Power Generation | Power Trading | Power Trading and Generation both | 3
Day3 | As per IEGC, Under Frequency Relays (UFRs) are to be provided for | Day to Day Load shedding to mange Load by States/UTs | Preventing the grid from cascade tripping and Grid Disintegration/ Grid Collapse | Protection of the Transmission Lines | Protection of Transformers | 2
Day3 | As per IEGC, Regional grids are to be operated as power pools | With centralised scheduling by RLDCs | With centralized scheduling by RLDC and NLDC | with decentralized scheduling and despatch, | None of these | 3
Day3 | Switching in/out of all 400 kV bus or line Reactors throughout the grid and Tap changing on all 400/220 kV ICTs shall be done | As per RLDCs instructions only. | As per decision by respective transmission Utility | As per decision by CTU | Any time as per decision by CPCC | 1
Day3 | As per IEGC who is responsible for discharging all functions of planning and co-ordination relating to inter-State transmission system in co-ordination with various agencies | Regional Power Committee (RPC) | Regional Load Despatch Centre (RLDC) | Central Transmission Utility (CTU) | Central Electricity Authority (CEA) | 3
Day3 | As per IEGC, Automatic Under-Frequency and df/dt Relays for load shedding in their respective systems are to be provided by | All SEBs, Distribution licensees and STUs | CTU and all STUs | Distribution licensees and STUs | CTU and all SEBs | 3
Day3 | After sheduling of forced outage of a unit under STOA(TGNA), RLDC shall inform about the revised schedule to -------- | Seller | Buyer | Seller and Buyer | Either seller or Buyer | 3
Day3 | Automatic Voltage Regulator with digital control shall be mandatory in the generating unit of above | 500MW | 200 MW | 100 MW | 250 MW | 3
Day3 | Grid Connectivity Standards make it mandatory to have ‘two sets of batteries, each equipped with its own charger’ for sub-stations of | 220 kV and above | 132 kV and above | 66 kV and above | 400 kV and above | 2
Day3 | Request for making connection to inter state transmission system is to be made to | CTU | CEA | The licensee with whose system the inter-connection is proposed | CERC | 1
Day3 | The limit specified for the power factor of the distribution system and bulk consumer is | Not mentioned in CEA’s technical standards | Not less than 0.95 | Not less than 0.9 | Not less than 0.85 | 2
Day3 | AC Substations of 220 kV rating Auxilary supply shall be arranged from ……… independent sources of High Tension(HT) feeders | two | one | one with two LT transformers | Three | 1
Day3 | The governers of HYDRO generating units shall have a droop of …. | 5-10% | 5-8% | 4-6% | 3-6% | 4
Day3 | The penalty for non-compliance of CEA's Regulations can be imposed by | CEA | Appropriate Commission | Ministry of Power | Appellate Tribunal for Electricity | 2
Day3 | In a grid disturbance, generation loss is 19% but load loss is 22%. This grid disturbance will be classified as | GD 3 | GD 2 | GD 20 | Can't say | 1
Day3 | Mock exercises for fire fighting shall be conducted by the entities, ___ | once every 3 months | once every 6 months | once a year | once in 2 years | 3
Day3 | With reference to CEA's Grid Connectivity Standards, the preferable switching scheme for a 132 kV substation is: | main and transfer scheme | double main and transfer scheme | one and half breaker scheme | double bus double breaker scheme | 1
Day3 | The total harmonic distortion in 220 kV system shall not exceed: | 1.5% | 2% | 2.5% | 5% | 3
Day3 | The maximum possible voltage unbalance in 400 and 765 kV shall be: | 2% | 1.5% | 3% | 5% | 2
Day3 | The governor of a partially loaded generator senses that the frequency dipped from 50.0 to 49.9 Hz. As a result of governor action, the load angle of the machine will | increase | decrease | remain constant | decrease by 10 degrees | 1
Day3 | The reason that several generators on one bus of same capacity can operate at different power outputs while remaining interconnected and synchronised is that these are operating at different ____ | speeds | load angles | frequencies | voltages | 2
Day3 | To increase the power output from a generator, which one of the following actions should be performed? | increase the terminal voltage | increase the excitation | Increase the power input to the prime mover | Increase the terminal voltage and increase the excitation | 3
Day3 | What possible problems could be caused by continous low frequency operation, say 48Hz on a 50Hz system? | Gain of time on synchronous clocks | possible damage to turbine blades due to vibration at low speed | certain customers' equipment will run at higher than normal speed | None of these | 2
Day3 | If the speed droop of a 50Hz machine is 4%. What frequency drop must occur to effect a 25% load increase on that machine? | 2.0 Hz | 1.0 Hz | 0.5 Hz | 0.25Hz | 3
Day3 | If the system frequency is at 49.0 Hz then the RPM of a cylindrical rotor machine is ____ | 3000 | 2940 | 3060 | 2880 | 2
Day3 | Saturation of the core of a power transformer increases with ____ in frequency and _____ in voltage. | increase, decrease | increase, increase | decrease, decrease | decrease, increase | 4
Day3 | The kVAr rating required for improving the power factor of a load operating at 1000 kW and 0.8 power factor to 0.9 is ________. | 100 kVAr | 500 kVAr | 50 kVAr | 250 kVAr | 4
Day3 | Which of the following is/are the function/s of the series compensation (TCSC) ? | prevents the voltage collapse in heavily loaded lines | controls the power flow through parallel lines | controls the receiving end voltage | all of these | 4
Day3 | Match the FACTs controllers and their targets a)SVC,b)PST,c)TCSC::1)Load angle,2)Line reactance,3)Receiving end voltage | a-1,b-3,c-2 | a-3, b-1, c-2 | a-2,b-3,c-1 | a-3,b-2,c-1 | 2
Day3 | The transmission capacity of a transmission line with a SIL of P0 and a series compensation of Kse, is: | P0/Sqrt(1-Kse) | P0*Sqrt(1-Kse) | P0 * (1-Kse) | P0/(1-Kse) | 1
Day3 | The nearest kVAr compensation required for improving the power factor of a 500 kW load from 0.8 lag to unity power factor is | 375 kVAr | 100 kVAr | 500 kVAr | 250 KVAr | 1
Day3 | Real power output from a generator with respect to its excitation: ____ | directly proportional | inversely proportional | it remains unchanged | excitation is fixed and cannot be changed | 3
Day3 | Charging current in the transmission line _____ | lags the voltage by 90 degrees | leads the voltage by 45 degrees | leads the voltage by 90 degrees | leads the voltage by 180 degrees | 3
Day3 | Why are shunt reactors connected at receiving end of long transmission line system? | To increase terminal voltage | To compensate voltage rise caused by capacitive charging at light load | To improve power factor | To reduce the fault current | 2
Day3 | Safety Interlocks in Control schemes are: a) Isolator Open/Close possible only if CB is open b) E/S closing possible only when isolator is open | (a) only | (b) only | both (a) and (b) | Neither (a) nor (b) | 3
Day3 | Match the device numbers of relays: (a)distance (b) instantaneous over current (c) time delayed overcurrent (d) differential :: (1) 21; (2) 87; (3) 51; (4) 50 | a-1;b-2;c-3;d-4; | a-1; b-4; c-3; d-2 | a-4; b-3; c-1; d-2; | a-3; b-2; c-1; d-4; | 2
Day3 | The inrush current in a transformer contains predominantly | 7th harmonic | 2nd harmonic | 5th Harmonic | 3rd harmonic | 2
Day3 | Dead time for autoreclose is: | 1 minute | 1 sec | 5 minute | 10 milli sec | 2
Day3 | The time delay for Zone-3 in distance protection is: | 100-200 ms | 350-400ms | 1000-1200ms | 0 ms | 3
Day3 | Negative sequence Protection is used for: | Line | Transformer | Generator | Busbar | 3
Day3 | What Type of Auto-Reclosing arrangement is used in Indian Power System? | High Speed Single pole reclosing (HSAR) | High Speed Three pole reclosing (HTAR) | Delayed Three Pole reclosing (DAR) | Delayed auto reclosing (DAR) with dead line (DL) and synchronism check (SC) | 1
Day3 | The loss of field of a generator results in generator | stalling | running as induction generator | running as synchronous motor | over speeding | 2
Day3 | The extent of unbalance in the Generator / Motor currents are indicated by ______currents | Positive sequence | Negative sequence | Harmonic | Saturation | 2
Day3 | The winding of the transformer which may be used for protection as well as for serving load is called the ________ winding | Primary | Secondary | Tertiary | Auxiliary | 3
Day3 | Generally, a highly conneted substation has _________fault level. | High | Low | zero | Infinite | 1
Day3 | What is "NOT" an advantage of the switching substation? | Avoid switching surges | Easy segregation of faulty zones | Can be used as a pooling point | Feeding power to the local area | 4
Day3 | What is the primary function of earth mat in a substation? | To act as a foundation for all equipments | To act as a deterrent to rodents | To limit step and touch potential for substation staff | Provide a high impedance path to the fault currents | 3
Day3 | Surge arresters are provided to | Limit the fault current | To limit the voltage | To divert lightning surges to ground | To absorb switching, lighting surges and discharge | 4
Day3 | In a substation all non current carrying parts shall be connected to | Adjacent equipment | Separate Earth electrodes | Earth mat | Need not be earthed | 3
Day3 | Scada Functions are: | Data Acquisition | Data Processing | Alarms | All of the above | 4
Day3 | Define the range of values that SCADA uses to determine whether the value retrieved for the analog is realistic. | Normal limit | Reasonability Limit | Forbidden Limit | Dead band Limits | 2
Day3 | What type of flag appears when data is uninitialised ? | Good | Suspect | Calculated | Garbage | 4
Day3 | Breaker and switch status, Line analog parameters,Transformer analog parameters are the types of _____ | Distribution Data | Power Plant Data | Substation Data | System Operational Data | 3
Day3 | Historical data recording allows you to preserve time series of ____ | Analog | Digital | Both Analog and digital | only counter data | 3
Day3 | The assumption in Real Time Power system application of State Estimation are: | Voltage and current waveform are purely sinusoidal | Balanced 3 Ph System | 3 Ph. System described by positive sequence network | All of these | 4
Day3 | Which of the following is not taken as an input by the State Estimator application? | Voltage | Frequency | Reactive Power | Active Power | 2
Day3 | Which forecasting is useful in real-time operations? | Short Term Forecasting | Medium Term Forecasting | Long Term Forecasting | Very long term | 1
Day4 | As per Sharing of Inter State Transmission Charges and Losses Regulations, which part of bill handles the charges on account of deviations from approved injection / withdrawal? | Third | Fourth | First | Second | 1
Day4 | Waiver of transmission charges allowed for the following with conditions on date of COD, award of construction contracts etc | REGS & RHGS | ESS chaerged with energy sourced from REGS & RHGS | Generation based on hydro power sources | All of these | 4
Day4 | RPCs shall issue RTDA (Regional Transmission Deviation Account) for the month of February 2021 to all designated ISTS Customers, CTU and other ISTS Licensees during……… | 1st week of March 2021 | 1st week of April 2021 | 15th of March 2021 | 31stof March 2021 | 4
Day4 | Monthly Transmission Charges for GNA in ISTS is expressed in……… | Rs/MWh | Rs/MW | Rs/MW/Day | Rs | 2
Day4 | Transmission deviation rate in Rs/MW/time block for a state or any other DIC located in the state for a time block shall be | Monthly Transmission Charges applicable to the particular drawee DIC | 1.05 X (total transmission charges for all drawee DICs located in the State, (as calculated in accordance with Regulation 5 to 8 of these regulations) for the billing month in Rs.)/ (GNA and GNARE quantum in MW of such entities located in the State, considered for billing, for the corresponding billing period X number of days in a month X 96).” | 1.25 X (total transmission charges for all drawee DICs located in the State, (as calculated in accordance with Regulation 5 to 8 of these regulations) for the billing month in Rs.)/ (GNA and GNARE quantum in MW of such entities located in the State, considered for billing, for the corresponding billing period X number of days in a month X 96).” | 1.20 X (total transmission charges for all drawee DICs located in the State, (as calculated in accordance with Regulation 5 to 8 of these regulations) for the billing month in Rs.)/ (GNA and GNARE quantum in MW of such entities located in the State, considered for billing, for the corresponding billing period X number of days in a month X 96).” | 3
Day4 | Which agreement the connectivity grantee signs with the nodal agency? | Power Purchase Agreement (PPA) | Transmission Service Agreement (TSA) | Bulk Power Agreement (BPA) | Connection Agreement | 4
Day4 | As per the provisions, T-GNA and T-GNARE charges collected in a billing month shall be reimbursed during the subsequent month in proportion to share in the | First Bill | Second Bill | Third Bill | Sum of First and Third Bills | 1
Day4 | Who is responsible for issuance of monthly regional transmission accounts? | RPC | RLDC | CERC | SERC | 1
Day4 | Who will pay the transmission deviation charges on account of deviation beyond approved GNA plus GNARE | A drawee DIC which is a regional entite | States and Generatings stations | A drawee DIC which is a regional entite but not covered under state | All of these | 4
Day4 | As per the provisions, T-GNA and T-GNARE charges collected in a billing month shall be reimbursed during the subsequent month for | States | Drawee DICS | Generators | A&C | 2
Day4 | Talcher-Kolar HVDC Charges are shared by the entities of……. | 70% to be shared by SR DICs & 30% to be shared by all DICs | 30% to be shared by SR DICs & 70% to be shared by all DICs | 100% to be shared by SR DICs | 100% to be shared by all DICs | 1
Day4 | T-GNA rates in Rs/MW/time block is calculated as | Transmission charges for all drawee DICs located in the State, for the billing month, (in rupees) / (number of days in a month X 96 X GNA and GNARE quantum , in MW, for all such drawee DICs located in the State considered for billing, for the corresponding billing period). | Transmission charges for all drawee DICs located in the State, for the billing month (in rupees) X 1.05 / (number of days in a month X 96 X GNA and GNARE quantum , in MW, for all such drawee DICs located in the State considered for billing, for the corresponding billing period). | Transmission charges for all drawee DICs located in the State, for the billing month (in rupees) X 1.10 / (number of days in a month X 96 X GNA and GNARE quantum , in MW, for all such drawee DICs located in the State considered for billing, for the corresponding billing period). | Transmission charges for all drawee DICs located in the State, for the billing month (in rupees) X 1.25 / (number of days in a month X 96 X GNA and GNARE quantum , in MW, for all such drawee DICs located in the State considered for billing, for the corresponding billing period). | 3
Day4 | Who will take the final decision, in case of dispute regarding basic network, nodal generation or nodal demand used in POC charges computation | Implementation Committee | Validation Committee | NLDC | CEA | 3
Day4 | Who will notify monthly transmission charges | CERC | RPCs | CEA | NLDC | 4
Day4 | As per sharing of ISTS charges regulation 2020, peak block in a month is | the time block in which national peak demand occurs | the time block in which ISGS injection is maximum | the sum of net ISTS drawal of all states is maximum | Non of these | 3
Day4 | In case of delay in issuance of RTA(Regional Transmission Account), provisional bills can be raised by | RPC only | NLDC | CTU | Nodal Agency | 3
Day4 | Methodology used for computing usage based part of AC system component of monthly ISTS charges is | Average participation methods | Marginal participation method | Hybrid methodology of average and marginal participation methods | Power tracing | 3
Day4 | ISTS losses shall not be applicable for | Injection schedules of DICs | Drawal schedules of DICs | Both A&B | None of these | 1
Day4 | YTC (Yearly transmission charges) of Mundra - Mohindergarh (to the extent of 1005MW) is included under which component of transmission charges | NC | RC | TC | NC&RC | 1
Day4 | YTC for STATCOM & SVC are included under | NC | RC | TC | AC-UBC | 2
Day4 | Under sharing of ISTS charges regulations 2020 basic network used for carrying out power flow studies is | 220kV and above network | 132kV and above network | 400kV and above network | 110kV and above network | 4
Day4 | CTU raises RTA & RTDA bills for the month of March 2021 during……...week of May 2021 | 1st & 2nd respectively | both in 1st week | 1st & 3rd respectively | 1st & 4th respectively | 2
Day4 | CTU raises bill for adjustments / revisions on | once in six moths | once in two months | once in three months | once in a year | 3
Day4 | Transmission charges for drawal of start up power are charged | based on transmission charge rate of the home state | 1.05 times transmission charge rate of home state | 1.2 times transmission charge rate of home state | transmission charges not applicable | 2
Day4 | As per the sharing of ISTS charges regulation 2020, the third bill is in respect of transmission charges bill for | transmission charges GNA | GNA plus T-GNA | adjustments & revisions | RTDA | 4
Day4 | Peak block of billing period is published by NLDC on the………of the month following the billing period | 7th day | 10th day | 1st day | 15th day | 3
Day4 | Time line for NLDC to notify monthly transmission charges by………day of the month following the billing period | 7th day | 10th day | 15th day | 25th day | 4
Day4 | T-GNA rates in Rs/MW/time block published for | all states | all generators & all states | All Drawee DICs | all target region generators | 1
Day4 | Transmission charges for GNA/GNARE computed for | all states | all drawee DICs within a state | all regional entities | B&C | 4
Day4 | Transmission charges for T-GNA payable by | DISCOMs | Generators | Embedded entities in states | B&C | 4
Day4 | Regional entity Generating station (a) drawing start-up power prior to COD or (b) drawing auxiliary power before or after COD through ISTS, shall pay transmission charges for such drawl | No transmission charges | T-GNA Rate for the State in which it is located | 50 % of T-GNA Rate for the State in which it is located | 10 % of T-GNA Rate for the State in which it is located | 2
Day4 | A generating station injecting infirm power before COD has to pay transmission charges | No transmission charges | T-GNA Rate for the State in which it is located | 50 % of T-GNA Rate for the State in which it is located | 10 % of T-GNA Rate for the State in which it is located | 1
Day4 | What is the Weekly Settlement Period of Deviation Charges ? | Tuesday to Monday | Monday to Sunday | Every Wednesday | Sunday to Saturday | 2
Day4 | Which of the following statements is true w.r.t sign convention of Deviation Charges | For a generator +ve sign indicates under generation & for a beneficiary –ve sign indicates over drawal. | For a generator +ve sign indicates over generation & for a beneficiary +ve sign indicates overdrawal. | For a generator, -ve sign indicates over generation & for a beneficiary –ve sign indicates under drawal. | For a generator, +ve sign indicates under generation & for a beneficiary –ve sign indicates under drawal. | 2
Day4 | As per CERC Deviation Settlement Mechanism Regulations, a 'WS Seller' means: | A generating station based on wind or solar or hybrid of wind & solar | A trader | A generator whose tariff is fixed by Commission. | A generator under ABT. | 1
Day4 | What is meant by Administered Price Mechanism | A mechanism to fix Deviation Charges. | A mechanism similar to ABT. | A mechanism in which prices of Coal, gas and other fuels are fixed at regulated rates for power generating purpose. | Price discovery in power exchange. | 3
Day4 | Which of these prepares Deviation Charges accounts? | RLDC | RPC | CEA | SLDC | 2
Day4 | Deviation charges collected from regional entities by RLDCs shall be credited to | Regional Deviation Charges Account | Reginal Deviation Charges and Ancillary Service pool Account | PSDF | Ancillary Service pool Account | 2
Day4 | What is the due date for Deviation Charges payments from the date of issue of the Deviation Charges A/c? | 10 days | 12 days | 7 days | 14 days | 3
Day4 | What is the interest payable for delay in Deviation Charges payment? | 0.04% per month | 0.04% per day compound interest | 0.4% per day simple interest | 0.04% per day simple interest | 4
Day4 | Any regional entity which at any time during the previous financial year fails to make payment of charges for deviation within the time specified in these regulations, shall be required to open a Letter of Credit (LC) equal to | 150% of their average payable weekly liability for deviations in the previous financial year | 110% of their average payable weekly liability for deviations in the previous financial year | 100% of their average payable weekly liability for deviations in the previous financial year | 110% of their average payable weekly liability for deviations in the previous three financial years | 2
Day4 | As per CERC Order dated 06.02.23, in case of forced outage of a seller, the charges for deviation shall be | At the reference charge rate, for a maximum duration of eight time blocks | At the reference charge rate, until the revision of its schedule | At the reference charge rate, for a maximum duration of eight time blocks or until the revision of its schedule, whichever is earlier | At the reference charge rate, for a maximum duration of six time blocks | 3
Day4 | As per DSM regulations 2022 & related orders, the infirm power injected into the grid by a generating unit of a generating station during the testing period, prior to COD of the unit shall be paid at | Reference Charge Rate | Contract Rate | Weighted Average ACP of the Day Ahead market segments of all power exchangers | zero | 4
Day4 | When the grid frequency is above 50.05 Hz, the general seller other than an ROR generating station or a generating station based on municipal solid waste shall be paid back for deviation by way over injection | At 50% of reference charge rate | At 20% of reference charge rate | At 10% of reference charge rate | zero | 4
Day4 | Who computes time block wise deviations for regional entities ? | RPC | RLDC | CERC | None of these | 2
Day4 | Any drawal of power by a generating station prior to COD of a unit for the startup activities shall | Pay no deviation charges | Pay at normal rate of charge for deviation | Pay at 50 % of normal rate of charge for deviation | Pay at 105 % of normal rate of charge for deviation | 2
Day4 | When the grid frequency is below 49.9 Hz, the charges for deviation corresponding to time block shall be payable by a Buyer who is an RE rich state ? | 120 % of normal rate of charge | 125 % of normal rate of charge | 150 % of normal rate of charge | 200 % of normal rate of charge | 4
Day4 | As per DSM regulations and CERC order dated 6th Feb 2023 on DSM, buyers are categorised as | Category 1: Buyer (other than the buyer with schedule less than 400 MW and the RE-rich State) Category 2: Buyer (with schedule up to 400 MW) | Category 1: Buyer (other than the buyer with schedule less than 400 MW and the RE-rich State) Category 2: Buyer being an RE rich state with RE generation greater than 3000 MW | Category 1: Buyer (other than the buyer with schedule less than 400 MW and the RE-rich State) Category 2: Buyer (with schedule up to 400 MW) Category 3: Buyer (being an RE Rich State) | Category 1: Buyer (other than the buyer with schedule less than 400 MW and the RE-rich State) Category 2: Buyer (with schedule up to 400 MW) Category 3: Buyer (being an RE Rich State) Category 4: Buyer being an RE rich state with RE generation greater than 3000 MW | 3
Day4 | The charges payable for deviation from schedule by the wind generators as WS - Seller for under injection between 15 % and 20 % of DWS | linked with frequency | At 10% of contract rate or in the absence of a contract rate, at the weighted average ACP of the Day Ahead Market segments of all Power Exchanges | At 20% of contract rate or in the absence of a contract rate, at the weighted average ACP of the Day Ahead Market segments of all Power Exchanges | At 50% of contract rate or in the absence of a contract rate, at the weighted average ACP of the Day Ahead Market segments of all Power Exchanges | 2
Day4 | As per CERC order dated 6th Feb 2023 on DSM regulation, normal rate of charges for deviation for a time block shall be equal to | the higher of [the weighted average ACP of the Day Ahead Market segments of all the Power Exchanges; and the weighted average ACP of the Real Time Market segments of all the Power Exchanges, for that time block] subject to a ceiling of Rs 12 per kWh | the higher of [the weighted average ACP of the Day Ahead Market segments of all the Power Exchanges; and the weighted average ACP of the Real Time Market segments of all the Power Exchanges, for that time block] | the higher of [the weighted average ACP of the Day Ahead Market segments of all the Power Exchanges; and Weighted Average Ancillary Service Charge of all the regions] for that time block | the higher of [the weighted average ACP of the Day Ahead Market segments of all the Power Exchanges; and Weighted Average Ancillary Service Charge of all the regions] for that time block, subject to a ceiling of Rs 12 per kWh | 1
Day4 | Congestion charge would be levied for | Under drawl in the importing control area | Over drawl in the importing control area | Under drawl or Over drawl in the importing control area | No congestion charges for importing control area | 2
Day4 | Congestion charges are paid | If lieu of deviation charges | In addition to the deviation charges | In lieu of reactive energy charges | In lieu of PoC charges | 2
Day4 | Congestion is a situation where the demand for transmission capacity | Exceeds the ATC | Equals the ATC | Less than Reliability Margin | Less than the ATC | 1
Day4 | NLDC/ RLDC(s) shall issue a notice for application of congestion charge if congestion persists for | 2 time-blocks not counting the time-block in which warning notice was issued by RLDC | 1 time-blocks counting the time-block in which warning notice was issued by RLDC | 2 time-blocks counting the time-block in which warning notice was issued by RLDC | 4 time-blocks not counting the time-block in which warning notice was issued by RLDC | 1
Day4 | No congestion charge levied for congestion in a transmission corridor, if congestion has been caused by | Forced outages of a line | Real-time power flow along a corridor exceeds the ATC | Grid voltage in the important nodes downstream/ upstream of the corridor is beyond the operating range | All of these options | 1
Day4 | Competitive Bidding guidelines have been framed under which provisions of the Electricity Act' 03 ? | Section 62 | Section 60 | Section 61 | Section 63 | 4
Day4 | According to competitve bidding guidelines issued by Ministry of Power, at the bid evaluation stage, ratio of minimum and maximum capacity charge (including both the non-escalable component and the escalable component incorporating escalation as per index being used for the purpose of evaluation) over the term of the Power Purchase Agreement (PPA) shall not be less than | 0.7 | 0.8 | 0.6 | 0.85 | 1
Day4 | The first stage of AUFLS (Automatic Under Frequency Load Shedding Scheme) in India is at ________ . | 49.6 | 49.5 | 49.4 | 49.3 | 3
Day4 | The last stage of AUFLS (Automatic Under Frequency Load Shedding Scheme) in India is at ________ . | 48.8 | 48.6 | 48.4 | 48.2 | 1
Day4 | Nodal agency for crises management is _______ | CEA | NLDC | CERC | CTU | 2
Day4 | Nodal Agency for implementation and operation of NOAR is _______ | CERC | CEA | NLDC | RPC | 3
Day4 | The registration for NOAR platform is valid for ______ years . | 3 Years | 1Year | 2 Years | 5 Years | 1
Day4 | Disbersement of transmission charges and operating charges is done NOAR by _______ . | RPC | Nodal RLDC | SLDC | NLDC | 4
Day4 | Issuance of standing clearance for a new OA user by concerned SLDC is ______ . | 3 Days | 5 Days | 7 Days | 1 Day | 3
Day4 | Violation of Terms and condtions of Standing clearance in any time block results in debaring the entity from transacting from power market for ______ . | 1 Month | 15 Days | 1 Year | 7 Days | 4
Day4 | In Case of congestion E-Bidding can be done on NOAR platform for ______. | Advance Bilateral STOA | Collective transaction in DAM & RTM of PX | FCFS Bilateral STOA | Day-Ahead Bilateral STOA | 1
Day4 | The contribution of inertia for the grid can be availed through ______ . | BESS (Battery Energy Storage System) | FESS (Flywheel Energy Storage System) | Flow Batteries | Electro-chemical Capaciters | 2
Day4 | Which of the following has higher Energy Density ? (i) Battery (ii) Electro-chemical Capacitors (iii) Conventional Capacitors | (i)>(ii)>(iii) | (ii)>(i)>(iii) | (iii)>(ii)>(i) | All | 1
Day4 | The Energy stored in a conventional capacitor is _______ . (i) Directly proportional to surface area of plates. (ii) Inversely proportional to surface area of plates. (iii) Directly proportional to charge seperation distance. (iv) Inversely proportional to charge seperation distance. | (ii) & (iv) | (i) & (iv) | (ii) & (iv) | (ii) & (iii) | 2
Day4 | A 100 MW battery at 50 % SOC (State of Charging) can pick up full capacity of 100 MW within _______ . | 1 Min | 5 Min | 30 Sec | 1 Sec | 4
Day4 | For fast charging of EV battery it is preferable to use the following : | AC Level 1 | AC Level 2 | DC Level 1 | DC Level 2 | 4
Day4 | What is the significance of Cut off date? | The owner of asset can start billing from that date | additional capitalisation would be allowed upto this date for a new project. | last date for filing tariff petition | last date for completing all expenditure. | 2
Day4 | Gross calorific value is measured in _____ | Kcal/kg of coal | kcal/lit of liquid fuel | kcal/m3 of gas | All of these | 4
Day4 | Expenditure towards initial spares is a part of _______ | O&M charges | Annual fixed charges | Capital cost | Working capital | 3
Day4 | A company had invested Rs.40 cr. from its own resources; if the total cost of the project is Rs.100 cr. What is the amount admissible as equity ? | Rs. 80 cr. | Rs.30 cr. | Rs.20 cr | Rs.70 cr. | 2
Day4 | A company had taken a loan of Rs.60 cr. and invested Rs.40 cr. from own resources. What is the treatment of loan component? | Rs.70 cr. treated as loan at SBI PLR | Rs.60 cr. is treated at actual rate of interest and Rs.10 cr. at normative interest rate | Rs.70 cr treated as loan at actual interest rate | Rs.70 cr at wt. average rate of interest | 2
Day4 | O&M expenses of a generating station are recovered through ____ | annual fixed charges | energy charges | working capital | maintenance spares | 1
Day4 | If 't' is the applicable tax rate, rate of pre-tax return on equity is _____ | base rate of ROE x (1-t) | base rate of ROE x (1+t) | base rate of ROE/(1+t) | base rate of ROE / (1-t) | 4
Day4 | Depreciation is calculated as a percentage of ….. | Loan component | Equity | Capital cost | Working capital | 3
Day4 | Normative O&M expenditure of a Sub-station | Decreases with increase in voltage level | Increases with increase in voltage level | Not related to voltage level | is a percentage of capital cost | 2
Day4 | Energy charges shall be payable by every Beneficiary as per | Share allocation | Total energy schedule in the month on ex power plant | Total energy scheduled in the month on ex-periphery of the beneficiary | Total drawal schedule of beneficiary including all contracts | 2
Day4 | Pick up the right order of stations with respect to auxiliary consumption. | Hydro>gas>coal>lignite | Coal>gas>hydro>lignite | Lignite>coal>gas>hydro | Gas>hydro>lignite>coal | 3
Day4 | Useful life of AC Substations is | 25 years | 35 years | 20 years | depends on voltage level | 1
Day4 | Initial Spare allowed for Transmission lines as % of capital cost is | 1% | 5% | 0.75% | 3.5% | 1
Day4 | Normative Annual Transmission System Availability factor is 95% for | AC Substation | AC Transmission Line | None of these | HVDC bi-pole link and HVDC Back-to-Back Substation | 4
Day4 | How many days are allowed to the beneficiary for payment of bill raised by transmission licensee without surcharges | 30 days | 60 days | 45 days | 90 days | 3
Day4 | How the benefits of refinancing of debt is to be shared between beneficiary and utility | 2:1 | 1:01 | Only beneficiary | Only Utility | 2
Day4 | Guideline for tariff determination is given in following section of Electricity Act,2003 | Section 15 | Section 79 | Section 61 | Section 178 | 3
Day4 | A petition can be filed in the Commission for tariff determination of a transmission project | After commissioning of Assets | At the time of project approval | 60 days before anticipated commissioning | One year before the Commissioning | 3
Day4 | Who shall certify the Monthly Availability factor of Transmission system | GM, NLDC | Chief (Engg), CERC | Member Secretary, RPC | Chairperson, CEA | 3
Day4 | Maximum Initial spares as % of capital cost are allowed for | HVDC Station | Static synchronous capacitors | Gas Insulated Sub-station - Green Field | Thermal-Coal Station | 2
Day4 | Interim truing up of the tariff for 2019-24 shall be carried out | During 19- 20 | During 2021 - 22 | During 2020 - 21 | No truing up of tariff is required in 2019-24 period | 2
Day4 | Truing up of the tariff for 2019-24 shall be carried out | During 21- 22 | During 2024 - 25 | A&B | No truing up of tariff is required in 2019-24 period | 3
Day4 | Truing up of the tariff for 2019-24 shall be carried out | During 19- 20 | During 2023 - 24 | During 2020 - 21 | During 2024 - 25 | 4
Day4 | Replacement of switchyard equipment in case of fault level increase is allowed under additional capitalization after cut off date | Yes | Depends on No. of circuits and voltage | Allowed only after prior approval of commission | Allowed after CEA approval | 1
Day4 | Case - I competitive bidding is meant for | Procurement of power from sources which are fuel specific | Procurement of power from sources which are location specific | Procurement of power from sources which are neither fuel specific nor location specific | Procurement of power from traders only | 3
Day4 | For the purpose of meeting Renewable Purchase Obligation (RPO) | Only distribution licensee is considered to be obligated entity | Only open access consumer is considered to be obligated entity | Only consumer of captive generation connected to grid is considered to be obligated entity | Distribution licensee, open access consumer and consumer of captive generation connected to grid are considered to be obligated entities | 4
Day4 | Central Government can give directions to Central Commission | On any issue it considers fit | On policy issues which involve public interest | On tariff issue only | On non-tariff issues only | 2
Day4 | In interest on working capital, two month receivable means | Fixed and energy charges of two month | Interest of two months | Salary of employees for two months | Spares for two months | 1
Day4 | If the station COD is 3.1.2020 then what would be the cut off date | 31.1.2023 | 31.3.2021 | 31.3.2022 | 31.1.2021 | 1
Day4 | What is norm of Maintenance spares for the gas based stations in working capital calculations | 25% of O&M expenses | 20% of O&M expenses | 30% of O&M expenses | 1% of the capital cost | 3
Day4 | If the GCV of the coal decreases during the month then the energy charges shall | decrease | increase | remain same | become zero | 2
Day4 | Which section of the Electricity Act 2003 empowers the appropriate commission to grant licence? | Section 42 | Section 29(2) | Section 14 | Section 12 | 3
Day4 | The total Capacity Charges receivable by a Generating station shall be shared by its Beneficiaries as per ______ | Average Requisitions | Average Share Allocation | Maximum Entitlement in peak hours | Maximum Entitlement in the month | 2
Day5 | In principle grant of connectivity by Nodal Agency , in case of requirement of ATS/Augmentation, is accorded in _____ Days . | 30 | 60 | 120 | 180 | 2
Day5 | Connectivity Bank Guarantee shall have to be submitted by an applicant in _______ number of parts . | 1 | 2 | 3 | 4 | 3
Day5 | Conn-BG3 to be furnished by the applicant after intimation of in-principle grant of Connectivity is _______ . | Rs. 1 lakh/MW | Rs. 2 lakh/MW | Rs. 4 lakh/MW | Rs. 1 lakh/MW | 2
Day5 | Conn-BG3 and Conn-BG2 shall be returned in equal parts over ______ years corresponding to the generation capacity which has been declared under commercial operation by the Connectivity grantee . | Three | Five | Seven | Ten | 2
Day5 | For seeking GNA to ISTS directly (not through STU) , the minimum requirement of load for distribution licenses or a bulk consumer is _______ . | 50 MW | 100 MW | 150 MW | None | 1
Day5 | Grant of GNA by Nodal Agency to entities other than STU shall be acorded as per the following time lines in cases involving no augmentaion required and augmentation required are ______ . | 120, 180 | 60, 120 | 30, 60 | 30, 180 | 4
Day5 | The notice period required for Relinquishment of Connectivity in full or in part is _______ . | 30 days | 3 Months | 6 Months | 1 Year | 1
Day5 | The Relinquishment charges in case of entities other than STU for Relinquishment of GNA shall be capped at _______ number of times the transmission charges last paid by the entity as per sharing regulation. | 12 | 24 | 72 | 84 | 2
Day5 | T-GNA can be applied for a minimum period of _____ . | one time block | 1 hour | 1 day | 6 time blocks | 1
Day5 | T-GNA can be applied up to _______ . | 3 Months | 1 Month | 11 Months | 12 Months | 3
Day5 | Advance apllication for grant of T-GNA can be made on the (D) day for grant of T-GNA starting on or after (D+3) day of _______ . | Same Month | Subsequent Month | Either Same or Subsequent Month | None | 3
Day5 | Advance Application for T-GNA shall be processed latest by 23.59 hours of _______ day , (D) being the date of making of application. | D+7 | D+15 | D+30 | D+1 | 4
Day5 | Nodal Agency for grant of T-GNA in case of bilateral transcations is _______ | NLDC | RLDC in which drawal point is situated | CTU | RLDC to which application is made | 2
Day5 | T-GNA granted under advance category for a period not exceding 1 month can be revised with a notice period of a ______ . | 1 day | 3 days | 4 time blocks | cannot be revised | 4
Day5 | T-GNA granted under advance category for a period of more than one month can be revised for the balanced period, withy a prior notice of _______ | 1 week | 1 month | 3 days | cannot be revised | 2
Day5 | Transmission charge rate for T-GNA shall be published state wise for each month by _______. | RPC | CERC | CEA | NLDC | 4
Day5 | Transmission charge rate for T-GNA is published as _______ . | Rs/MW/time block | Rs/MW/hour | paise/KWH | paise/KW/time block | 1
Day5 | In case of transmission constraints the cuirtailment of T-GNA transactions be done in following order . | Bilateral, Collective under day ahead, Collective under real time market | Collective under day ahead, Bilateral, Collective under real time market | Collective under real time market, Collective under day ahead, Bilateral | All in pro-rata | 1
Day5 | The following entities are eligible to apply for grant of connectivity to ISTS. (i) Standalone ESS with installed capacity of 40 (ii) MW.Standalone ESS with installed capacity of 60 MW. (iii) Standalone ESS of 10 MW within aggregate installed capacity of 50 MW through Lead ESS. | (ii) only | (iii) only | (ii) and (iii) | All in pro-rata | 3
Day5 | The Following entities are eligible to apply for GNA. (i) Distribution lisencee with a load of 50 MW. (ii) STU on behalf of intra-State entity with a load of 40 MW. (iii) Transmission licencee conected to ISTS. | (i) only | (ii) only | (iii) only | All three | 4
Day5 | At what RMS voltage level is VARh recorded by SEM? | More than 103% and less than 97% | less than 103% and more than 97% | At all voltage levels | None of the above | 1
Day5 | Where are the main meters (SEM) installed in case of ISGS (Regional Entity) injection? | All GTs | All outgoing feeders | All GTs and Station Transformers | All Station transformers | 2
Day5 | Which part of ABT is calculated / accounted for, by SEM? | Energy Charge | Capacity Charge | Deviation charge | Net input output charges | 3
Day5 | SEMs have two standard models with voltage and current ratings of ______ | 110V,1A & 110V,5A | 64V,1A & 64V,5A | 110V,5A & 64V, 1A | 110V,1A&64V,5A | 1
Day5 | For which of the following meters, the same core of CT & PT is used? | Main & Standby Meter | Check & Standby Meters | Main & Check meters | Main, Check and Standby meters | 3
Day5 | Through which device can limited time synchronization of SEM be done? | SEM itself | Data Collecting Device (DCD) | PC | GPS | 2
Day5 | As per IEGC, by when should the SEM data be sent to respective RLDCs every week? | Tuesday noon | Thursday noon | Monday noon | Sunday Noon | 1
Day5 | Which meters are used in computation, in case of failure of Main meters ? | Check meters first followed by standby if check is not available | Standby meters first followed by check if standby is not available | Wait for rectification of main meters | Average of check and stand by meters | 1
Day5 | For which of the following is Cumulative energy registered? | Reactive High & Low energy | Active Energy | Active, Reactive High & Reactive Low energy | Only active energy | 3
Day5 | What are SEMs used for energy accounting known as? | Interface meters | Consumer meters | Energy Accounting meters | Audit Meters | 1
Day5 | 400/220 kV ICT has got two meters, Meter-A & Meter-B installed at HV & LV side respectively. Which of the following statement is true? | Meter-A is main meter & Meter-B is Check meter | Meter-A is main meter & Meter-B is standby meter | Meter-B is main meter & Meter-A is Check meter | Meter-A is check meter and Meter -B is standby Meter | 2
Day5 | How is collection of SEM data by DCD done under S/D condition of that particular feeder? | Removing the meter & reconnecting in the lab | Using internal Battery backup | By giving external supply to the meter | Both B and C | 4
Day5 | Bids on a constant volume in MWh/h at a certain price in a defined period of consecutive hours, with a condition of "all or none" is known as, ____ | Single-interval bid | Portfolio bid | Block bid | Reserve bid | 3
Day5 | For Collective transactions,Transmision losses shall be absorbed by | Buyer of electricity only | Seller of electricity only | Buyer and Seller of electricity | Buyer or Seller of electricity | 1
Day5 | Nodal agency for Collective Transactions is | SLDC | RLDC | NLDC | CTU | 3
Day5 | One of the Salient feature of Power Exchange operation in India | Mandatory participation | Uniform pricing | Pay-as bid pricing | Single sided bidding | 2
Day5 | Power Exchange(s) carry out congestion management in Day Ahead Market using | Counter-trading | Market splitting | Explicit auction | redispatching | 2
Day5 | The Day-ahead market in Power Exchange is | Capacity based market | Energy only market | Mix of Capacity based and Energy only market | None of these | 2
Day5 | Which of the following most appropriately defines"Term Ahead market” | A market where physical delivery of electricity occurs more than one day (T + 2 or more) ahead from the date of transaction (T) | A market where physical delivery of electricity occurs either on the same day as the date of the transaction (T) or on the next day (T+ 1) | A market where physical delivery of electricity occurs more than two days(T + 3 or more) ahead from the date of transaction (T) | more than four day (T + 5 or more) ahead from the date of transaction (T) | 1
Day5 | Which of the following represents a congestion management method where auctioning of the available inter-connector capacity is carried out and the capacity reservation is done on the basis of the highest bids received? | Counter-trading | Market splitting | Re-dispatching | Explicit Auction | 4
Day5 | Which type of Bidding Mechanism is prevalent for Day Ahead Market in a Power Exchange? | single sided open auction | double sided open auction | single sided closed auction | double sided closed auction | 4
Day5 | What is the relation between wind velocity and power? | proportional to square of velocity | inversely proportional to cube of velocity | no relation at all | proportional to cube of velocity | 4
Day5 | What is the definition of Penetration level of Wind source ? | percentage wind energy in design energy | percentage wind energy in annual energy | percentage wind energy in total energy of control Area. | percentage wind energy in total energy of the country. | 3
Day5 | One REC is issued for an injection of ________ energy | 100MWh | 100 kWh | 1000MWh | 1MWh | 4
Day5 | What is the Pf range in which Wind generators are to operate? | 0.8 pf lag to 0.9 pf lead | 0.95pf lag to 0.95pf lead | 0.8 lag to 0.8 pf | 1pf lag and lead | 2
Day5 | What is the minimum voltage at which WTG can disconnect under Fault Ride Through condition? | below 10% | below 85% | below 15% | below | 3
Day5 | What is the short circuit contribution of WTG? | Nil | it depends on direct connection or AC-DC-AC connection | infinite | very less | 2
Day5 | What is the inertia contribution of type 4 (Full conversion) WTG? | nil | very less | it depends on rotor winding | it depends on rotor mass | 1
Day5 | A Renewable Energy generator sells power of 1500 MWh to a Discom @ 3.50 ps/u a preferential rate fixed by the SERC. How many Renewable Energy Certificates will the generator get? | 1500 | 1500000 | 15 | Nil | 4
Day5 | Renewable Energy Certificates are traded at the Power Exchanges on | every Wednesday of the month | every last Wednesday of the month | every day | every first Wednesday of the month | 2
Day5 | Which of the following hydro generators are eligible for Renewable Energy Certificates? | less than 25 MW | less than 10 MW | less than 1 MW | all hydro projects are eligible | 1
Day5 | What is the denomination of each REC issued? | 1 MWh | 5 KWh | 5MWh | 1 KWh | 1
Day5 | Which Agency has been designated as Central Agency under REC Mechanism? | SLDC | SERC | NLDC | Ministry of Power | 3
Day5 | Accreditation and Registration under REC Mechanism are valid for: | 3 Years | 6 Months | 5 Years | 1 Year | 3
Day5 | Which one of the following is the correct sequence of ‘Process under REC Mechanism’? | Accreditation, Registration, Issuance, Redemption | Redemption, Issuance,Registration, Accreditation | Accreditation, Redemption, Issuance, Redemption | Issuance, Registration, Accreditation, Redemption | 1
Day5 | RECs can be purchased by: | Mandatory Buyers | Voluntary Buyers | Voluntary and Mandatory Buyers | Power Exchanges Only | 3
Day5 | All RE generators shall apply for issuance of REC within ---------- period of generation. | 1 month | 2 months | 3 months | 6 months | 4
Day5 | NLDC Charges and Corporate Office Expenses shall be apportioned to RLDCs on the basis of __________ | no. of states in their jurisdiction | Demand served in the respective Region | Peak shortage in the respective region | Installed capacity in the respective region | 2
Day5 | The One-time fees for registration of DISCOMs with RLDCs is _________ | 15 lacs | 10 lacs | 20 lacs | 8 lacs | 2
Day5 | The one-time fees for registration of power exchanges with NLDC is _________ | 15 lacs | 10 lacs | 20 lacs | 8 lacs | 3
Day5 | The LDC Charges for the distribution licensees and buyers shall be determined on the basis of | (1/3) of annual charges | (1/2) of annual charges | (2/3) of annual charges | None of the Above | 1
Day5 | RLDCs or NLDC shall be be allowed to recover incentive of 15% of Annual LDC Charges for aggregate performance level of | 85% | 90% | 95% | 100% | 2
Day5 | The employees of RLDC, NLDC & SLDC who acquire the certificate of basic level, specialist level and management level in their respective areas of specialization shall be allowed retainer-ship amount /month(Rs) during the validity of such certificate period as | 7500, 10000, 12000 | 7000, 10000, 12000 | 8500, 10000, 12000 | 6000, 7500, 10000 | 1
Day5 | As per RLDC Fees & Charges Regulatuions, What is Late Payment surcharges/month applicable for delay in payment by RLDC users | 1% | 1.25% | 1.5% | 1.75% | 3
Day5 | As per the CERC's Notification for RLDC Fees and Charges (Generating Stations + Sellers), (Distribution Licensees + Buyers) and Inetrstate Transmission Licensee share the Annual LDC Charges each at the rate of: | 50% | 30% | 45% | 33.33% | 4
Day5 | As per RLDC Fees & Charges Regulation 2019, Generating station upto 10 MW installed capacity shall pay fees for User registration of Rs | 0.10 Lac | 0.50 Lac | 1.0 Lac | 2.0 Lac | 2
Day5 | As per RLDC Fees & Charges Regulation 2019, Generating station having installed capacity of more than 2000 MW shall pay fees for User registration of Rs | 1.0 Lac | 2.0 Lac | 5.0 Lac | 10.0 Lac | 4
Day5 | As per RLDC Fees & Charges Regulation 2019, the inter-State trading licensees, sellers and buyers shall pay one time user registration fees of Rs. | 0.1 Lac | 0.50 Lac | 1.0 Lac | 2.0 Lac | 1
Day5 | As per Fees & Charges regulation, What is the rebate allowed to user if payment is made within (T+5) days | 1% | 1.25% | 1.5% | 2% | 3
Day5 | Services rendered by LDCs comprises of ___ | System Operation | Market Operation | Logistics | All of these | 4
Day5 | What are the expenses identified under a separate head for the first time in the RLDC Fees and Charges order by CERC? | Return on Equity | Interest on Loan | Depreciation | HR Expenses | 4
Day5 | As per RLDC Fees and Charges Regulation 2019, Which of the following source of income can not be deposited in Contingency Reserve Account | Registration Fees | STOA application fees | STOA operating charges | REC and PAT charges | 1
Day5 | Any shortfall in meeting the revenue expenditure including HR expenses shall be met from | LDCD Fund | PSDF Fund | SCED | Reactive Pool | 1
Day5 | Which of the following is/are the roles played by the System Operator in Electric Supply Industry in India? | Agents for achieving economy and efficiency | Change agent for catalysing the ongoing reforms process | Agents for providing feedback to policy makers, planners and regulators | All of these roles | 4
Day5 | Switching Operations are performed by: | ISO | TSO | Both ISO and TSO | Neither ISO nor TSO | 2
Day5 | Maintenance of Transmission Assets is carried out by: | ISO | TSO | Both ISO and TSO | Neither ISO nor TSO | 2
Day5 | Who owns the Transmission assets ? | ISO | TSO | Both ISO and TSO | Neither ISO nor TSO | 2
Day5 | Which of the following is a statutory function ? | Generation | Transmission | Distribution | System Operation | 4
Day5 | Which of the following DOES NOT discharge statutory functions? | CTU | System Operators | Generation | STU | 3
Day5 | How many components are there in Annual LDC Charges for RLDC Fees & Charges | 8 | 7 | 6 | 5 | 1
Day5 | Protocols used for synchrophasor communication | IEEE C37.118-2011 | IEC 61850-90-5 | IEEE C37.242-2013 | both a &b | 4
Day5 | Benefits of synchrophasor technology | High resolution data | Time stamping | Direct Node Angle measurements | All of these | 4
Day5 | Which of the following signals available from a PMU? | Analog Output | Analog Input | Digital Input & output | All of these | 4
Day5 | With reporting rate of PMU as 25 frames per second, what is the maximum oscillation frequency it can detect? | 25Hz | 12.5Hz | 6.25Hz | 50Hz | 2
Day5 | The minimum number of satelites required for a PMU to time stamp the phasor data | 4 | 3 | 1 | 5 | 2
Day5 | Which of these is not a function of PDC? | Collecting data from PMU | Time allignment of data obtained from PMU | Time stamping of data arrived from PMU | Facilitating data to Historian | 3
Day5 | Phasor Measurement Unit(PMU) shall report data in …….. Interval. | Microseconds | Milliseconds | Nano Seconds | Second | 2
Day5 | In which time format PMU Time stamping to phasor data is done? | Coordinated Universal Time(UTC) | Indian Standard Time(IST) | Both a & b | Greenwich Mean Time (GMT) | 1
Day5 | Wide Area Monitoring System (WAMS) can provide…….. type of data | Time aligned phasor data | Time Skewed data | Non simultaneous data | All of the above | 1
Day5 | In a typical PMU from which parameter Frequency is calculated? | R Phase Voltage Angle | Positive Sequence voltage Angle | Positive Sequence Current Angle | R Phase Current Angle | 2
Day5 | Normally Signal Sampling during Phasor Estimation in PMU shall be in the range of … | 10Hz -50 Hz | In the order of kHz | 50 Hz – 100 Hz | 0-10 Hz | 2
Day5 | Controls in Scada system are implemented using: | Communication Channel | Remote Terminal Units (RTU) | Human Machine Interface(HMI) | All of these options | 4
Day5 | Which of these are components of Data Aquisition system? | Sensors/transducers | Communication Channel | Analog-to-digital converters | All of these options | 4
Day5 | Scada Functions are: | Data Acquisition | Data Processing | Alarms | All of these options | 4
Day5 | What is the system that provides the inter-connection of all the servers, workstation, peripherals with redundant ethernet switch? | WAN | LAN | DMZ | none of these options | 2
Day5 | What is the system that monitors the interfaces to the SCADA/EMS servers, workstations, devices, all SCADA/EMS gateway and routers and gathers performance statistics like resource utilisation? | WAN | LAN | NMS | Operator Console | 3
Day5 | Which is not a protocol used by RTU for communicating with control centre? | Profibus | Modbus | CIM | IEC 60870-5-101 | 3
Day5 | Define the range of values that SCADA uses to determine whether the value retrieved for the analog is realistic. | Normal limit | Reasonability Limit | Forbidden Limit | Dead band Limits | 2
Day5 | Which is the function that allows you to store time series of any set of analog, status, and accumulator SCADA measurements, as well as changes to limits on recorded analog measurements? | Historical Data Management System | Network Management System | Operator Console | Human Machine Interface | 1
Day5 | 'Milli seconds accurate time of status changes' for devices monitored, is provided by which application? | Historical Data Recorder | Sequence of Events | Network Management System | Human Machine Interface | 2
Day5 | Digital data is acquired in SCADA, ____ | Periodically | By Exception | Floating | none of these options | 2
Day5 | In general, what is the periodicity of Analog data scan? | Below 10 seconds | 15 to 20 seconds | 30 to 40 seconds | more than 1 minute | 1
Day5 | What is the full form of RTU? | Remote Telemetry Unit | Regional Telemetry Unit | Remote Terminal Unit | Regional Terminal Unit | 3
Day5 | In PLCC what is the maximum speed of data transfer? | 100 kbps | 500 kbps | 1200 kbps | 1000 kbps | 3
Day5 | If a line flow crosses its raw high/low limits then data quality is _____ | Good | Suspect | Replace | None of the above | 2
Day5 | Which of the following data can be retrieved from HDR ? | Only Analog | Only Digital | Only Analog & Digital | none of these options | 3
Day5 | What type of flag appears when data is uninitialised ? | Good | Suspect | Calculated | Garbage | 4
Day5 | Remote Suspect means value suspect at? | Control center where RTU is reporting | Local Control center | Any where | none of these options | 1
Day5 | If the data is not retrieved in last scan it is marked as _____ | Over range | Bad | Uninitialized | none of these options | 2
Day5 | Which of these is not part of SLDC/RLDC SCADA system? | Data Server | ISR server | Resource Server | ICCP server | 3
Day5 | What is the advantage of SCADA system? | Access the monitored system measurands both periodically and instantaneously | Display trends of the measurands over a span of time. | Initiates alarms for the abnormal states of devices. | All of these options | 4
Day5 | What are the components required for basic SCADA functions? | Sensors, RTU | Communication network | SCADA master Station | All of these options | 4
Day5 | Which system is also known as one on one system? | Single master Single remote | Single Master Multiple Remote | Multiple Master Multiple Remote | none of these options | 1
Day5 | Breaker and switch status, Line analog parameters,Transformer analog parameters are the types of _____ | Distribution Data | Power Plant Data | Substation Data | System Operational Data | 3
Day5 | The MMI data presentation is basically _____ | visual | recorded | audible. | All of these options | 4
Day5 | Major source of telemetry error in SCADA systems are ____ | Poor precision class of CT & PT | Non linearity in output of transducer | Poor precision class of CT & PT & Non linearity in output of transducer | none of these options | 3
Day5 | What are the basic instruments installed at site for measurement of voltage & current? | Energy Meter | Wave Trap | CT & PT | Transducer | 3
Day5 | Output of transducer is ______ | 2-10 mA | 4-30mA | 4-20mA | 0-9mA | 3
Day5 | RTU's are installed in Power System at | Transmission Line | Substations | Control Centre | B & C | 4
Day5 | What does ISR stand for? | Information Storage & Data Redundant system | Information Storage & Data Retrival system | Intelligent Storage & Data Retrival system | none of these options | 2
Day5 | Which database is generally used in ISR server for storage of information? | Oracle | Java | C++ | MS Windows | 1
Day5 | What does DMZ stand for? | De-Magnetise Zone | De-Militarized Zone | De-Monitoring Zone | none of these options | 2
Day5 | What does telemetry refer to? | Technique of receiving information or data | Technique of transfering information or data | Technique of receiving information or data & Technique of transfering information or data | none of these options | 3
Day5 | Data is transmitted through medium like: | PLCC | VSAT | Optical Fibre | All of these options | 4
Day5 | Typical configuration of SCADA systems are: | Point to point | Point to Multipoint | Point to point & Point to Multipoint | none of these options | 3
Day5 | Historical data recording allows you to preseve time series of ____ | Analog | Digital | Analog & Digital | none of these options | 3
Day5 | SCADA is defined as a…………….. | Process model | Logic Model | Intergration of Process Model & Logic Model | All of these options | 3
Day5 | Output of Trnasducer is connected to…….. | Analog input in RTU | Digital input in RTU | C&R Pannel | All of these options | 1
Day5 | SCADA is called Supervisory because…. | It has in-direct control over the process | Direct control over the process | Loop Control | All of these options | 1
Day5 | Optical Fiber communication can be affected by…. | EMI | High Voltage | weather conditions | none of these options | 4